## Project Overview
BESS SIZING CHALLENGE — SAMPLE DATASET
Mavuno Foods Ltd ¦ Nairobi Industrial Area, Kenya
COMPANY PROFILE
Company | Mavuno Foods Ltd |  | Registered food processor, Nairobi Industrial Area
Sector | Food & Beverage Manufacturing |  | Grain milling, packaging, cold storage
Operating hours | 05:00 – 22:00 | hrs | Mon–Sat; reduced Sunday (06:00–14:00)
Grid connection | 33 kV / 415 V |  | KPLC metered supply, SC5 tariff category
Installed PV | 200 | kWp | Rooftop mono-PERC, installed Nov 2022, south-facing 15° tilt
PV inverter | SMA Sunny Tripower |  | 4 × 50 kW string inverters, no battery storage currently
Grid reliability | ~72 hrs/month outages |  | Frequent load-shedding; diesel genset 150 kVA backup
Diesel cost | 145 | KES/litre | Current pump price; ~80 L/hr consumption under full load
TARIFF STRUCTURE — KPLC SC5 (Large Commercial / Industrial)
Energy charge — peak | 21.5 | KES/kWh | 06:00–22:00 (16 hrs/day)
Energy charge — off-peak | 10.2 | KES/kWh | 22:00–06:00 (8 hrs/day)
Fuel cost adjustment (ERC) | 3.2 | KES/kWh | Applied uniformly, reviewed quarterly
ERC levy | 0.3 | KES/kWh | Energy Regulatory Commission
Effective peak tariff (all-in) | 25 | KES/kWh | Sum of above during peak hours
Demand charge | 850 | KES/kVA/month | Based on highest 30-min kVA in billing month
Fixed charge (meter rent) | 2200 | KES/month
Exchange rate reference | 129.5 | KES/EUR | For equipment cost benchmarking
CHALLENGE BRIEF
OBJECTIVE: Using the data provided in this workbook, design a BESS solution for Mavuno Foods Ltd that: 1. Maximises self-consumption of PV generation (currently ~35% is exported to grid at minimal feed-in tariff) 2. Performs peak shaving to reduce the monthly demand charge 3. Provides backup autonomy of at least 2 hours for critical loads (~45 kW: cold storage + control systems) 4. Achieves payback within 8 years at current tariff levels DELIVERABLE: Build a tool (HTML/React/Python app) that takes the inputs from this dataset, calls an AI API, and returns a recommended BESS power (kW), capacity (kWh), estimated annual savings, and payback period. Bonus: show 3 scenarios (conservative / recommended / aggressive) and a daily charge-discharge strategy.

## Hourly Data
Day | Day Type | Hour | Time | Load (kW) | PV Gen (kW) | Net Load (kW) | Grid Import (kW) | PV Surplus (kW) | Notes
1 | Monday | 0 | 00:00 | 41.8 | 0 | 41.8 | 41.8 | 0 | Off-peak
1 | Monday | 1 | 01:00 | 38.2 | 0 | 38.2 | 38.2 | 0 | Off-peak
1 | Monday | 2 | 02:00 | 39.7 | 0 | 39.7 | 39.7 | 0 | Off-peak
1 | Monday | 3 | 03:00 | 39.3 | 0 | 39.3 | 39.3 | 0 | Off-peak
1 | Monday | 4 | 04:00 | 42.4 | 0 | 42.4 | 42.4 | 0 | Off-peak
1 | Monday | 5 | 05:00 | 59.1 | 0 | 59.1 | 59.1 | 0 | Off-peak
1 | Monday | 6 | 06:00 | 72.4 | 20.4 | 52 | 52 | 0 | Peak
1 | Monday | 7 | 07:00 | 85.5 | 36.7 | 48.8 | 48.8 | 0 | Peak
1 | Monday | 8 | 08:00 | 89 | 62.9 | 26.1 | 26.1 | 0 | Peak
1 | Monday | 9 | 09:00 | 90.8 | 86.1 | 4.7 | 4.7 | 0 | Peak
1 | Monday | 10 | 10:00 | 94.5 | 113.3 | -18.8 | 0 | 18.8 | Peak ¦ PV surplus
1 | Monday | 11 | 11:00 | 89 | 131.5 | -42.5 | 0 | 42.5 | Peak ¦ PV surplus
1 | Monday | 12 | 12:00 | 77.9 | 133.3 | -55.4 | 0 | 55.4 | Peak ¦ PV surplus ¦ PV peak
1 | Monday | 13 | 13:00 | 89.8 | 132.3 | -42.5 | 0 | 42.5 | Peak ¦ PV surplus
1 | Monday | 14 | 14:00 | 90.6 | 110.2 | -19.6 | 0 | 19.6 | Peak ¦ PV surplus
1 | Monday | 15 | 15:00 | 96.4 | 87.2 | 9.2 | 9.2 | 0 | Peak
1 | Monday | 16 | 16:00 | 91.3 | 59.6 | 31.7 | 31.7 | 0 | Peak
1 | Monday | 17 | 17:00 | 93.6 | 41.3 | 52.3 | 52.3 | 0 | Peak
1 | Monday | 18 | 18:00 | 77.8 | 25.5 | 52.3 | 52.3 | 0 | Peak
1 | Monday | 19 | 19:00 | 72.2 | 0 | 72.2 | 72.2 | 0 | Peak
1 | Monday | 20 | 20:00 | 55.8 | 0 | 55.8 | 55.8 | 0 | Peak
1 | Monday | 21 | 21:00 | 52.3 | 0 | 52.3 | 52.3 | 0 | Peak
1 | Monday | 22 | 22:00 | 41.3 | 0 | 41.3 | 41.3 | 0 | Off-peak
1 | Monday | 23 | 23:00 | 43 | 0 | 43 | 43 | 0 | Off-peak
2 | Tuesday | 0 | 00:00 | 41.7 | 0 | 41.7 | 41.7 | 0 | Off-peak
2 | Tuesday | 1 | 01:00 | 43.2 | 0 | 43.2 | 43.2 | 0 | Off-peak
2 | Tuesday | 2 | 02:00 | 41.5 | 0 | 41.5 | 41.5 | 0 | Off-peak
2 | Tuesday | 3 | 03:00 | 42.2 | 0 | 42.2 | 42.2 | 0 | Off-peak
2 | Tuesday | 4 | 04:00 | 38.3 | 0 | 38.3 | 38.3 | 0 | Off-peak
2 | Tuesday | 5 | 05:00 | 56.4 | 0 | 56.4 | 56.4 | 0 | Off-peak
2 | Tuesday | 6 | 06:00 | 68.7 | 22.2 | 46.5 | 46.5 | 0 | Peak
2 | Tuesday | 7 | 07:00 | 84.4 | 40.5 | 43.9 | 43.9 | 0 | Peak
2 | Tuesday | 8 | 08:00 | 89.4 | 68.9 | 20.5 | 20.5 | 0 | Peak
2 | Tuesday | 9 | 09:00 | 92.8 | 94.5 | -1.7 | 0 | 1.7 | Peak ¦ PV surplus
2 | Tuesday | 10 | 10:00 | 91.9 | 120 | -28.1 | 0 | 28.1 | Peak ¦ PV surplus
2 | Tuesday | 11 | 11:00 | 93.3 | 142.3 | -49 | 0 | 49 | Peak ¦ PV surplus
2 | Tuesday | 12 | 12:00 | 76.7 | 145.6 | -68.9 | 0 | 68.9 | Peak ¦ PV surplus ¦ PV peak
2 | Tuesday | 13 | 13:00 | 89.4 | 138.4 | -49 | 0 | 49 | Peak ¦ PV surplus
2 | Tuesday | 14 | 14:00 | 90.8 | 125.8 | -35 | 0 | 35 | Peak ¦ PV surplus
2 | Tuesday | 15 | 15:00 | 94.5 | 96 | -1.5 | 0 | 1.5 | Peak ¦ PV surplus
2 | Tuesday | 16 | 16:00 | 94.8 | 70.6 | 24.2 | 24.2 | 0 | Peak
2 | Tuesday | 17 | 17:00 | 93.2 | 41.6 | 51.6 | 51.6 | 0 | Peak
2 | Tuesday | 18 | 18:00 | 73.2 | 24.1 | 49.1 | 49.1 | 0 | Peak
2 | Tuesday | 19 | 19:00 | 70.6 | 0 | 70.6 | 70.6 | 0 | Peak
2 | Tuesday | 20 | 20:00 | 51.3 | 0 | 51.3 | 51.3 | 0 | Peak
2 | Tuesday | 21 | 21:00 | 55.7 | 0 | 55.7 | 55.7 | 0 | Peak
2 | Tuesday | 22 | 22:00 | 43.3 | 0 | 43.3 | 43.3 | 0 | Off-peak
2 | Tuesday | 23 | 23:00 | 39.9 | 0 | 39.9 | 39.9 | 0 | Off-peak
3 | Wednesday | 0 | 00:00 | 41.9 | 0 | 41.9 | 41.9 | 0 | Off-peak
3 | Wednesday | 1 | 01:00 | 40.4 | 0 | 40.4 | 40.4 | 0 | Off-peak
3 | Wednesday | 2 | 02:00 | 43.5 | 0 | 43.5 | 43.5 | 0 | Off-peak
3 | Wednesday | 3 | 03:00 | 40.8 | 0 | 40.8 | 40.8 | 0 | Off-peak
3 | Wednesday | 4 | 04:00 | 39.6 | 0 | 39.6 | 39.6 | 0 | Off-peak
3 | Wednesday | 5 | 05:00 | 56.5 | 0 | 56.5 | 56.5 | 0 | Off-peak
3 | Wednesday | 6 | 06:00 | 70.4 | 17.5 | 52.9 | 52.9 | 0 | Peak
3 | Wednesday | 7 | 07:00 | 86.5 | 36.3 | 50.2 | 50.2 | 0 | Peak
3 | Wednesday | 8 | 08:00 | 90.1 | 49.2 | 40.9 | 40.9 | 0 | Peak
3 | Wednesday | 9 | 09:00 | 96.6 | 72.5 | 24.1 | 24.1 | 0 | Peak
3 | Wednesday | 10 | 10:00 | 91.2 | 88.8 | 2.4 | 2.4 | 0 | Peak
3 | Wednesday | 11 | 11:00 | 88.4 | 108 | -19.6 | 0 | 19.6 | Peak ¦ PV surplus
3 | Wednesday | 12 | 12:00 | 77.8 | 111.7 | -33.9 | 0 | 33.9 | Peak ¦ PV surplus ¦ PV peak
3 | Wednesday | 13 | 13:00 | 85.4 | 106 | -20.6 | 0 | 20.6 | Peak ¦ PV surplus
3 | Wednesday | 14 | 14:00 | 94.5 | 92.6 | 1.9 | 1.9 | 0 | Peak
3 | Wednesday | 15 | 15:00 | 96.5 | 75.3 | 21.2 | 21.2 | 0 | Peak
3 | Wednesday | 16 | 16:00 | 90.8 | 53.2 | 37.6 | 37.6 | 0 | Peak
3 | Wednesday | 17 | 17:00 | 92.6 | 33.4 | 59.2 | 59.2 | 0 | Peak
3 | Wednesday | 18 | 18:00 | 74.6 | 20.5 | 54.1 | 54.1 | 0 | Peak
3 | Wednesday | 19 | 19:00 | 69.7 | 0 | 69.7 | 69.7 | 0 | Peak
3 | Wednesday | 20 | 20:00 | 52.6 | 0 | 52.6 | 52.6 | 0 | Peak
3 | Wednesday | 21 | 21:00 | 52.7 | 0 | 52.7 | 52.7 | 0 | Peak
3 | Wednesday | 22 | 22:00 | 43.7 | 0 | 43.7 | 43.7 | 0 | Off-peak
3 | Wednesday | 23 | 23:00 | 43.3 | 0 | 43.3 | 43.3 | 0 | Off-peak
4 | Thursday | 0 | 00:00 | 39.6 | 0 | 39.6 | 39.6 | 0 | Off-peak
4 | Thursday | 1 | 01:00 | 41 | 0 | 41 | 41 | 0 | Off-peak
4 | Thursday | 2 | 02:00 | 39.1 | 0 | 39.1 | 39.1 | 0 | Off-peak
4 | Thursday | 3 | 03:00 | 43.5 | 0 | 43.5 | 43.5 | 0 | Off-peak
4 | Thursday | 4 | 04:00 | 43.2 | 0 | 43.2 | 43.2 | 0 | Off-peak
4 | Thursday | 5 | 05:00 | 56.8 | 0 | 56.8 | 56.8 | 0 | Off-peak
4 | Thursday | 6 | 06:00 | 70.8 | 25.1 | 45.7 | 45.7 | 0 | Peak
4 | Thursday | 7 | 07:00 | 83.9 | 43.5 | 40.4 | 40.4 | 0 | Peak
4 | Thursday | 8 | 08:00 | 90.9 | 66.5 | 24.4 | 24.4 | 0 | Peak
4 | Thursday | 9 | 09:00 | 93.8 | 86.5 | 7.3 | 7.3 | 0 | Peak
4 | Thursday | 10 | 10:00 | 92.6 | 111.6 | -19 | 0 | 19 | Peak ¦ PV surplus
4 | Thursday | 11 | 11:00 | 93.3 | 136.7 | -43.4 | 0 | 43.4 | Peak ¦ PV surplus
4 | Thursday | 12 | 12:00 | 78 | 138.9 | -60.9 | 0 | 60.9 | Peak ¦ PV surplus ¦ PV peak
4 | Thursday | 13 | 13:00 | 85.3 | 136.7 | -51.4 | 0 | 51.4 | Peak ¦ PV surplus
4 | Thursday | 14 | 14:00 | 94.2 | 112.2 | -18 | 0 | 18 | Peak ¦ PV surplus
4 | Thursday | 15 | 15:00 | 93.6 | 87 | 6.6 | 6.6 | 0 | Peak
4 | Thursday | 16 | 16:00 | 95.3 | 66.4 | 28.9 | 28.9 | 0 | Peak
4 | Thursday | 17 | 17:00 | 89.3 | 41.2 | 48.1 | 48.1 | 0 | Peak
4 | Thursday | 18 | 18:00 | 76.3 | 22.3 | 54 | 54 | 0 | Peak
4 | Thursday | 19 | 19:00 | 74.2 | 0 | 74.2 | 74.2 | 0 | Peak
4 | Thursday | 20 | 20:00 | 52.5 | 0 | 52.5 | 52.5 | 0 | Peak
4 | Thursday | 21 | 21:00 | 51.3 | 0 | 51.3 | 51.3 | 0 | Peak
4 | Thursday | 22 | 22:00 | 41.2 | 0 | 41.2 | 41.2 | 0 | Off-peak
4 | Thursday | 23 | 23:00 | 42.4 | 0 | 42.4 | 42.4 | 0 | Off-peak
5 | Friday | 0 | 00:00 | 39.2 | 0 | 39.2 | 39.2 | 0 | Off-peak
5 | Friday | 1 | 01:00 | 39.9 | 0 | 39.9 | 39.9 | 0 | Off-peak
5 | Friday | 2 | 02:00 | 44 | 0 | 44 | 44 | 0 | Off-peak
5 | Friday | 3 | 03:00 | 41.9 | 0 | 41.9 | 41.9 | 0 | Off-peak
5 | Friday | 4 | 04:00 | 40.6 | 0 | 40.6 | 40.6 | 0 | Off-peak
5 | Friday | 5 | 05:00 | 58.1 | 0 | 58.1 | 58.1 | 0 | Off-peak
5 | Friday | 6 | 06:00 | 67.7 | 20.7 | 47 | 47 | 0 | Peak
5 | Friday | 7 | 07:00 | 85 | 39.8 | 45.2 | 45.2 | 0 | Peak
5 | Friday | 8 | 08:00 | 89.1 | 58.5 | 30.6 | 30.6 | 0 | Peak
5 | Friday | 9 | 09:00 | 91 | 86.5 | 4.5 | 4.5 | 0 | Peak
5 | Friday | 10 | 10:00 | 92 | 112.3 | -20.3 | 0 | 20.3 | Peak ¦ PV surplus
5 | Friday | 11 | 11:00 | 92.9 | 122.8 | -29.9 | 0 | 29.9 | Peak ¦ PV surplus
5 | Friday | 12 | 12:00 | 74.4 | 134 | -59.6 | 0 | 59.6 | Peak ¦ PV surplus ¦ PV peak
5 | Friday | 13 | 13:00 | 86.3 | 123.3 | -37 | 0 | 37 | Peak ¦ PV surplus
5 | Friday | 14 | 14:00 | 94.1 | 109.6 | -15.5 | 0 | 15.5 | Peak ¦ PV surplus
5 | Friday | 15 | 15:00 | 93.5 | 87.7 | 5.8 | 5.8 | 0 | Peak
5 | Friday | 16 | 16:00 | 95.6 | 58.2 | 37.4 | 37.4 | 0 | Peak
5 | Friday | 17 | 17:00 | 89.1 | 38.6 | 50.5 | 50.5 | 0 | Peak
5 | Friday | 18 | 18:00 | 75.5 | 22.6 | 52.9 | 52.9 | 0 | Peak
5 | Friday | 19 | 19:00 | 73.4 | 0 | 73.4 | 73.4 | 0 | Peak
5 | Friday | 20 | 20:00 | 54 | 0 | 54 | 54 | 0 | Peak
5 | Friday | 21 | 21:00 | 55.9 | 0 | 55.9 | 55.9 | 0 | Peak
5 | Friday | 22 | 22:00 | 38.6 | 0 | 38.6 | 38.6 | 0 | Off-peak
5 | Friday | 23 | 23:00 | 40.4 | 0 | 40.4 | 40.4 | 0 | Off-peak
6 | Saturday | 0 | 00:00 | 40 | 0 | 40 | 40 | 0 | Off-peak
6 | Saturday | 1 | 01:00 | 43.2 | 0 | 43.2 | 43.2 | 0 | Off-peak
6 | Saturday | 2 | 02:00 | 39.5 | 0 | 39.5 | 39.5 | 0 | Off-peak
6 | Saturday | 3 | 03:00 | 39.1 | 0 | 39.1 | 39.1 | 0 | Off-peak
6 | Saturday | 4 | 04:00 | 40.7 | 0 | 40.7 | 40.7 | 0 | Off-peak
6 | Saturday | 5 | 05:00 | 57.5 | 0 | 57.5 | 57.5 | 0 | Off-peak
6 | Saturday | 6 | 06:00 | 68.7 | 19 | 49.7 | 49.7 | 0 | Peak
6 | Saturday | 7 | 07:00 | 88.5 | 35.4 | 53.1 | 53.1 | 0 | Peak
6 | Saturday | 8 | 08:00 | 92.9 | 56.1 | 36.8 | 36.8 | 0 | Peak
6 | Saturday | 9 | 09:00 | 90.9 | 82.4 | 8.5 | 8.5 | 0 | Peak
6 | Saturday | 10 | 10:00 | 95.6 | 103.8 | -8.2 | 0 | 8.2 | Peak ¦ PV surplus
6 | Saturday | 11 | 11:00 | 93.3 | 118.7 | -25.4 | 0 | 25.4 | Peak ¦ PV surplus
6 | Saturday | 12 | 12:00 | 74 | 121.6 | -47.6 | 0 | 47.6 | Peak ¦ PV surplus ¦ PV peak
6 | Saturday | 13 | 13:00 | 86.3 | 115.1 | -28.8 | 0 | 28.8 | Peak ¦ PV surplus
6 | Saturday | 14 | 14:00 | 88.9 | 99.1 | -10.2 | 0 | 10.2 | Peak ¦ PV surplus
6 | Saturday | 15 | 15:00 | 96.6 | 76.5 | 20.1 | 20.1 | 0 | Peak
6 | Saturday | 16 | 16:00 | 95.4 | 55.3 | 40.1 | 40.1 | 0 | Peak
6 | Saturday | 17 | 17:00 | 91.1 | 39.6 | 51.5 | 51.5 | 0 | Peak
6 | Saturday | 18 | 18:00 | 79 | 21.4 | 57.6 | 57.6 | 0 | Peak
6 | Saturday | 19 | 19:00 | 73.3 | 0 | 73.3 | 73.3 | 0 | Peak
6 | Saturday | 20 | 20:00 | 50.9 | 0 | 50.9 | 50.9 | 0 | Peak
6 | Saturday | 21 | 21:00 | 51.8 | 0 | 51.8 | 51.8 | 0 | Peak
6 | Saturday | 22 | 22:00 | 43.8 | 0 | 43.8 | 43.8 | 0 | Off-peak
6 | Saturday | 23 | 23:00 | 41.5 | 0 | 41.5 | 41.5 | 0 | Off-peak
7 | Sunday | 0 | 00:00 | 43.3 | 0 | 43.3 | 43.3 | 0 | Off-peak
7 | Sunday | 1 | 01:00 | 44.5 | 0 | 44.5 | 44.5 | 0 | Off-peak
7 | Sunday | 2 | 02:00 | 40.3 | 0 | 40.3 | 40.3 | 0 | Off-peak
7 | Sunday | 3 | 03:00 | 43.5 | 0 | 43.5 | 43.5 | 0 | Off-peak
7 | Sunday | 4 | 04:00 | 43 | 0 | 43 | 43 | 0 | Off-peak
7 | Sunday | 5 | 05:00 | 45.1 | 0 | 45.1 | 45.1 | 0 | Off-peak
7 | Sunday | 6 | 06:00 | 60.9 | 28.4 | 32.5 | 32.5 | 0 | Peak
7 | Sunday | 7 | 07:00 | 63.5 | 39.8 | 23.7 | 23.7 | 0 | Peak
7 | Sunday | 8 | 08:00 | 69.2 | 67.1 | 2.1 | 2.1 | 0 | Peak
7 | Sunday | 9 | 09:00 | 68.8 | 89.4 | -20.6 | 0 | 20.6 | Peak ¦ PV surplus
7 | Sunday | 10 | 10:00 | 73.3 | 116 | -42.7 | 0 | 42.7 | Peak ¦ PV surplus
7 | Sunday | 11 | 11:00 | 71 | 137.6 | -66.6 | 0 | 66.6 | Peak ¦ PV surplus
7 | Sunday | 12 | 12:00 | 68.2 | 144.2 | -76 | 0 | 76 | Peak ¦ PV surplus ¦ PV peak
7 | Sunday | 13 | 13:00 | 66.2 | 140.2 | -74 | 0 | 74 | Peak ¦ PV surplus
7 | Sunday | 14 | 14:00 | 41.2 | 119.8 | -78.6 | 0 | 78.6 | Peak ¦ PV surplus
7 | Sunday | 15 | 15:00 | 41.4 | 91.6 | -50.2 | 0 | 50.2 | Peak ¦ PV surplus
7 | Sunday | 16 | 16:00 | 44 | 64.1 | -20.1 | 0 | 20.1 | Peak ¦ PV surplus
7 | Sunday | 17 | 17:00 | 41.9 | 44.4 | -2.5 | 0 | 2.5 | Peak ¦ PV surplus
7 | Sunday | 18 | 18:00 | 40.4 | 24.4 | 16 | 16 | 0 | Peak
7 | Sunday | 19 | 19:00 | 46 | 0 | 46 | 46 | 0 | Peak
7 | Sunday | 20 | 20:00 | 46 | 0 | 46 | 46 | 0 | Peak
7 | Sunday | 21 | 21:00 | 40.4 | 0 | 40.4 | 40.4 | 0 | Peak
7 | Sunday | 22 | 22:00 | 41.3 | 0 | 41.3 | 41.3 | 0 | Off-peak
7 | Sunday | 23 | 23:00 | 41.6 | 0 | 41.6 | 41.6 | 0 | Off-peak

## Monthly Billing
Month | Days | Total Cons (kWh) | Peak kWh | Off-peak kWh | PV Gen (kWh) | PV Self-use (kWh) | Grid Import (kWh) | Peak Demand (kVA) | Energy Bill (KES) | Demand Bill (KES) | Fixed (KES) | Diesel (KES) | Total Bill (KES) | Notes
Jan | 31 | 68200 | 49104 | 19096 | 7800 | 5070 | 63130 | 98 | 1489215 | 83300 | 2200 | 162400 | 1737115 | Dry season — high PV, stable grid
Feb | 28 | 62100 | 45333 | 16767 | 7200 | 4680 | 57420 | 95 | 1363033 | 80750 | 2200 | 116000 | 1561983 | Dry season
Mar | 31 | 71400 | 49980 | 21420 | 5800 | 3770 | 67630 | 100 | 1542954 | 85000 | 2200 | 255200 | 1885354 | Long rains begin — reduced PV
Apr | 30 | 70800 | 48144 | 22656 | 4900 | 3185 | 67615 | 102 | 1513987 | 86700 | 2200 | 440800 | 2043687 | Long rains peak — frequent outages
May | 31 | 69500 | 47955 | 21545 | 5200 | 3380 | 66120 | 99 | 1494041 | 84150 | 2200 | 359600 | 1939991 | Long rains easing
Jun | 30 | 65300 | 46363 | 18937 | 6400 | 4160 | 61140 | 96 | 1418512 | 81600 | 2200 | 139200 | 1641512 | Cool dry season
Jul | 31 | 66800 | 48096 | 18704 | 6600 | 4290 | 62510 | 97 | 1458645 | 82450 | 2200 | 127600 | 1670895 | Cool dry season — low temps, high cold storage load
Aug | 31 | 67200 | 48384 | 18816 | 6900 | 4485 | 62715 | 97 | 1467379 | 82450 | 2200 | 104400 | 1656429 | Dry season
Sep | 30 | 68400 | 49932 | 18468 | 7400 | 4810 | 63590 | 98 | 1501312 | 83300 | 2200 | 92800 | 1679612 | Dry — best PV month
Oct | 31 | 72100 | 50470 | 21630 | 5600 | 3640 | 68460 | 103 | 1558081 | 87550 | 2200 | 324800 | 1972631 | Short rains — demand peaks, grid stress
Nov | 30 | 71600 | 49404 | 22196 | 4800 | 3120 | 68480 | 104 | 1539185 | 88400 | 2200 | 406000 | 2035785 | Short rains peak
Dec | 31 | 67900 | 48209 | 19691 | 6800 | 4420 | 63480 | 96 | 1474992 | 81600 | 2200 | 174000 | 1732792 | Short dry spell — pre-holiday slowdown
TOTAL / AVG |  | 821300 | 581374 | 239926 | 75400 | 49010 | 772290 | 98.75 | 17821336 | 1007250 | 26400 | 2702800 | 21557786

## Tool Inputs
SUGGESTED TOOL INPUTS — extract these from the dataset above
Load & Tariff
Load & Tariff
avg_monthly_consumption_kwh | 68900 | kWh | Average monthly total consumption
peak_consumption_share | 0.71 | % | Share of energy consumed during peak hours
contracted_power_kva | 110 | kVA | Typical contracted capacity
peak_demand_kva | 100 | kVA | Average monthly peak demand
tariff_peak_kesh_kwh | 25 | KES | All-in peak tariff incl. levies
tariff_offpeak_kesh_kwh | 13.7 | KES | All-in off-peak tariff incl. levies
demand_charge_kesh_kva | 850 | KES | Monthly demand charge per kVA
peak_hours_per_day | 16 | hrs | 06:00–22:00
PV System
pv_installed_kwp | 200 | kWp | Rooftop monocrystalline PERC
avg_daily_pv_generation_kwh | 200 | kWh | Annual average (185 kWh dry / 165 kWh rainy)
pv_self_consumption_rate | 0.65 | % | Currently ~65% self-consumed, ~35% exported
avg_daily_surplus_kwh | 70 | kWh | PV generation not consumed by load
feed_in_tariff_kesh | 5 | KES | Approximate feed-in rate — very low incentive
Project Constraints & Objectives
backup_critical_load_kw | 45 | kW | Cold storage + control systems (always on)
backup_autonomy_target_hrs | 2 | hrs | Minimum backup during grid outages
max_payback_years | 8 | years | Client's maximum acceptable payback
bess_cost_reference_eur_kwh | 180 | EUR | Approximate LFP BESS installed cost/kWh
exchange_rate_kes_eur | 129.5 | KES | KES per EUR for cost conversion
project_lifetime_years | 15 | years | Standard BESS warranty horizon
annual_tariff_escalation | 0.06 | % | Historical KPLC annual tariff increase ~6%

## Instructions
CHALLENGE INSTRUCTIONS — BESS Sizing Tool
THE SCENARIO
Mavuno Foods Ltd is a food processing company in Nairobi's Industrial Area. They have a 200 kWp solar PV system on their roof, but ~35% of the solar energy is wasted because it can't be consumed in real time. They also face high electricity bills due to peak tariffs and demand charges, plus frequent grid outages that force them to run a diesel generator. Your task: design a BESS solution that solves all three problems simultaneously.
LEVEL 1 — BASIC TOOL
Step 1 | Open the 'Tool Inputs' sheet. These are the pre-processed key numbers extracted from the dataset.
Step 2 | Build a web tool (HTML/React/Python) with input fields pre-filled with these values.
Step 3 | When the user clicks 'Analyze', send the inputs to the Claude API with a well-crafted prompt.
Step 4 | Display the AI response as structured output: recommended kW, kWh, annual savings (KES), payback (years).
LEVEL 2 — ADVANCED TOOL (BONUS)
Step 5 | Load and parse the 'Hourly Data' sheet (168 rows = 7 days × 24 hours).
Step 6 | Plot the load curve vs PV generation curve to visually identify surplus windows and peak demand periods.
Step 7 | Calculate automatically: daily average surplus, peak demand hours, optimal charge/discharge windows.
Step 8 | Feed both the calculated stats AND a summary of the raw profile to the AI for a richer recommendation.
Step 9 | Show 3 BESS scenarios: Conservative (backup focus) / Recommended (balanced) / Aggressive (max savings).
TIPS FOR YOUR AI PROMPT
Tip 1 | Be explicit about units — the AI must distinguish kW (power) from kWh (energy).
Tip 2 | Include the tariff structure — the arbitrage opportunity between peak (25 KES) and off-peak (13.7 KES) is huge.
Tip 3 | Mention the backup requirement explicitly (45 kW critical load, 2 hrs minimum).
Tip 4 | Ask for reasoning, not just numbers — 'explain why you chose this capacity'.
Tip 5 | Request JSON output for easy parsing, then render it nicely in your UI.
Tip 6 | Consider adding: 'Assume LFP chemistry, 90% round-trip efficiency, 80% usable DoD, 6000 cycle lifetime'.
KEY NUMBERS TO KNOW
Daily PV surplus | ~70 kWh/day average (more in dry season, less during rains)
Peak demand to shave | ~100 kVA — even a 10% reduction saves ~85,000 KES/year in demand charges
Diesel cost context | ~72 hrs/month × 80 L/hr × 145 KES/L = ~835,000 KES/year in diesel alone
Tariff spread | 25.0 vs 13.7 KES/kWh = 11.3 KES/kWh arbitrage opportunity during off-peak charging
EXPECTED OUTPUT RANGE
Payback should land in the 5–9 year range depending on how you weight diesel savings.